## Slide 1: Scaling: Causes and Prevention
Larry Sutter
Materials Science & Engineering
Michigan Technological University

## Slide 2: Introduction
“Those who cannot remember the past are condemned to repeat it.”
George Santayana (1863 –1952)

## Slide 3: Introduction
“You can observe a lot by watching.”
Yogi Berra (1925 – 2015 )

## Slide 6
The 1956 unveiling of historical marker

## Slide 8
Granitoid was favored by the Village Council due to its low cost and durability
  Pavements constructed in Chicago were still in good condition after 8 years of service!

## Slide 12: Significance?
Why was this concrete so durable given it had no entrained air and it was in a severe F-T environment?
  The surface mortar was extremely dense and impermeable
    Low w/c, good densification, and wet cured
    Similar capillary porosity to UHPC
    High belite cement – similar to the use of SCMs
  Mortar layer protected lower quality concrete layer

## Slide 13: Important Considerations
The concrete constituents, proportions, and construction all influence durability
Water is needed for deleterious expansion to occur (permeability)
Severe environments are major contributors
  freezing and thawing, deicer applications, high sulfate soils, etc.
Strength does not equal durability – but it matters

## Slide 14
Deicer Scaling
Notes: Close-ups of pavement scaling showing exposed aggregate and delamination.

## Slide 15
Deicer Scaling
Notes: Close-ups of pavement scaling showing exposed aggregate and delamination.

## Slide 16
Deicer Scaling
Notes: Close-ups of pavement scaling showing exposed aggregate and delamination.

## Slide 17: Scaling
Typically appears within 1 to 5 years after construction
Deicer chemicals play a role
  Will amplify scaling deterioration (physical attack)
  Deicers can chemically react with hydrated paste constituents and degrade strength AND cause expansion (chemical attack)
Scaling prevented through proper air entrainment (hardened concrete) and a relatively low water-to-cement ratio
Minimize finishing, which can reduce air content at surface

## Slide 18: Scaling
Mechanism
  Not well understood

## Slide 19: Scaling
Mechanism
  Not well understood
  MORE RESEARCH IS NEEDED!!!

## Slide 20: Scaling
Mechanism
  Not well understood
  MORE RESEARCH IS NEEDED!!!
  Just kidding… but not really...
  Key need is to better understand prevention (sealers)

## Slide 21: Scaling
Mechanism
  Not well understood
  Predominately a physical attack
  Chemical attack (deicers) is also a contributor

## Slide 22
Mechanism
  Physical Attack
  Current research indicates scaling is due to tensile forces developed in the surface layer of concrete due to expansion of the ice layer (glue spalling)†
  The expansive forces of the ice are at a maximum when the solution freezing on the surface contains ~3% dissolved salt, and the type of salt is not a factor† (for physical attack)
† Valenza, J. J., and G. W. Scherer. 2007. A Review of Salt Scaling: II. Mechanisms, Cement and Concrete Research. 37(7), 1022-1034.

## Slide 23
Mechanism
  Physical Attack
  The mechanical properties of the ice layer are affected by brine pockets in the ice layer – expansive forces maximized with dilute brine solutions present†
  The strength of the concrete surface (resistance to expansion forces) is key to resisting the expansion
    High w/c = lower strength (blessing the concrete)
† Valenza, J. J., and G. W. Scherer. 2007. A Review of Salt Scaling: II. Mechanisms, Cement and Concrete Research. 37(7), 1022-1034.

## Slide 25
0.45 w/c
0.50 w/c

## Slide 26
0.45 w/c
0.50 w/c

## Slide 27: Role of Entrained Air
First a quick review of hardened cement paste microstructure

## Slide 29
Cement Hydration
Cement Grains
Water

## Slide 30
Cement Hydration
Early Hydration Products

## Slide 31
Later Hydration Products or “Outer Product”
Cement Hydration

## Slide 32
Capillary Pores
Cement Hydration

## Slide 33
Hydration products are porous (gel pores) causing permeability at a nano-scale
Cement Hydration

## Slide 34
Entrained Air Voids
Cement Hydration

## Slide 35: Role of Entrained Air
Air entrainment reduces bleeding
  Bleeding will increase the w/c in the surface layer
Ice formation in air voids sucks water from the surrounding capillary pores
  Creates a compression force that resists the tensile forces of the ice layer
  DON’T WORK THE AIR OUT OF THE SURFACE

## Slide 36
Small Bubbles, Lots of Them

## Slide 37
Impact of Poor Finishing
0.5 to 1 inch

## Slide 38: Take Aways – Physical Attack
Minimize potential for scaling attacks by reducing w/c
Recommend 0.45 maximum
Strongly suggest 0.42 maximum
MINIMIZE WATER ADDED TO SURFACE FOR FINISHING
Now…. chemical attack...

## Slide 39: Scaling
Mechanism
  Not well understood
  Predominately a physical attack
  Chemical attack (deicers) is also a contributor
    Again we need to discuss some basics of hydration chemistry…

## Slide 41
Portland Cement Reaction
  Cement + Water -> CSH + CH

## Slide 42
Portland Cement Reaction
  Cement + Water -> CSH + CH
CSH - Calcium Silicate Hydrate
  Provides strength
  In a perfect world cement hydration would be 100% CSH…

## Slide 43
Portland Cement Reaction
  Cement + Water -> CSH + CH
CH- Calcium Hydroxide
  Weak link
  Platy structure (like book pages), low strength
  Soluble in water
  Solubility maximum at the freezing point of water
  Dissolution of CH increases permeability

## Slide 44: Supplementary Cementitious Materials
Fly Ash Particles
Most less than 10 microns
Cement Particles
Most less than 45 microns

## Slide 45
Fly ash densifies hardened cement by physical effects (filler) and chemical effects (pozzolan)
Portland Cement Reaction
  Cement + Water -> CSH + CH
Pozzolanic Reaction
  CH + Pozzolan + Water -> CSH
  Pozzolanic reaction consumes (reduces) CH, produces CSH

## Slide 46: Supplementary Cementitious Materials
Slag Cement
  Similar to cement in composition
  Quenched > Glass > Reactive
  Produces less CH and consumes CH in its hydration reaction
Silica Fume
  Very fine particle size
  Very reactive
  $$

## Slide 47
Okay so why does all this talk about calcium hydroxide matter?

## Slide 48
Okay so why does all this talk about calcium hydroxide matter?
Calcium hydroxide is at the center of chemical deicer attack

## Slide 49: Cylinders exposed to MgCl2 solution after 84 days of constant low temperature test. From left to right: 0.40, 0.50, and 0.60 w/c

## Slide 50: Cylinders exposed to CaCl2 solution after 84 days of constant low temperature test. From left to right: 0.40, 0.50, and 0.60 w/c

## Slide 51: Cylinders exposed to NaCl solution after 84 days of constant low temperature test. From left to right: 0.40, 0.50, and 0.60 w/c

## Slide 52: Cylinders exposed to Ca(OH)2 solution after 84 days of constant low temperature test. From left to right: 0.40, 0.50, and 0.60 w/c

## Slide 53
Hi conc. CaCl2 – 500 days – 40 ºF

## Slide 54
Hi conc. MgCl2 – 500 days – 40 ºF

## Slide 55: Chemical Mechanisms of Deicer Attack
CaCl2 (Monosi & Collepardi, 1990)
  3Ca(OH)2 + CaCl2 + 12H2O  3CaO·CaCl2·15H2O
NaCl (Marchand 1994)
  2NaCl + Ca(OH)2  CaCl2 + 2NaOH
MgCl2 (Mindess, Young and Darwin, 2002)
  Ca(OH)2 + MgCl2  CaCl2 + Mg(OH)2
  C-S-H + MgCl2  CaCl2 + M-S-H

## Slide 56: Chemical Mechanisms of Deicer Attack
How Calcium Chloride (CaCl2) Attacks
  3Ca(OH)2 + CaCl2 + 12H2O  3CaO·CaCl2·15H2O
NaCl (Marchand 1994)
  2NaCl + Ca(OH)2  CaCl2 + 2NaOH
MgCl2 (Mindess, Young and Darwin, 2002)
  Ca(OH)2 + MgCl2  CaCl2 + Mg(OH)2
  C-S-H + MgCl2  CaCl2 + M-S-H
“Calcium Hydroxide”

## Slide 57: Chemical Mechanisms of Deicer Attack
How Calcium Chloride (CaCl2) Attacks
  3Ca(OH)2 + CaCl2 + 12H2O  3CaO·CaCl2·15H2O
NaCl (Marchand 1994)
  2NaCl + Ca(OH)2  CaCl2 + 2NaOH
MgCl2 (Mindess, Young and Darwin, 2002)
  Ca(OH)2 + MgCl2  CaCl2 + Mg(OH)2
  C-S-H + MgCl2  CaCl2 + M-S-H
“Calcium Chloride”

## Slide 58: Chemical Mechanisms of Deicer Attack
How Calcium Chloride (CaCl2) Attacks
  3Ca(OH)2 + CaCl2 + 12H2O  3CaO·CaCl2·15H2O
NaCl (Marchand 1994)
  2NaCl + Ca(OH)2  CaCl2 + 2NaOH
MgCl2 (Mindess, Young and Darwin, 2002)
  Ca(OH)2 + MgCl2  CaCl2 + Mg(OH)2
  C-S-H + MgCl2  CaCl2 + M-S-H
“Water”

## Slide 59: Chemical Mechanisms of Deicer Attack
How Calcium Chloride (CaCl2) Attacks
  3Ca(OH)2 + CaCl2 + 12H2O  3CaO·CaCl2·15H2O
NaCl (Marchand 1994)
  2NaCl + Ca(OH)2  CaCl2 + 2NaOH
MgCl2 (Mindess, Young and Darwin, 2002)
  Ca(OH)2 + MgCl2  CaCl2 + Mg(OH)2
  C-S-H + MgCl2  CaCl2 + M-S-H
“Calcium Oxychloride”

## Slide 60: Chemical Mechanisms of Deicer Attack
How Calcium Chloride (CaCl2) Attacks
  3Ca(OH)2 + CaCl2 + 12H2O  3CaO·CaCl2·15H2O
NaCl (Marchand 1994)
  2NaCl + Ca(OH)2  CaCl2 + 2NaOH
MgCl2 (Mindess, Young and Darwin, 2002)
  Ca(OH)2 + MgCl2  CaCl2 + Mg(OH)2
  C-S-H + MgCl2  CaCl2 + M-S-H
EXPANSIVE PHASE !!!

## Slide 61: Chemical Mechanisms of Deicer Attack
How Calcium Chloride (CaCl2) Attacks
  3Ca(OH)2 + CaCl2 + 12H2O  3CaO·CaCl2·15H2O
How Sodium Chloride (NaCl) Attacks
  2NaCl + Ca(OH)2  CaCl2 + 2NaOH
How Magnesium Chloride (MgCl2) Attacks
  Ca(OH)2 + MgCl2  CaCl2 + Mg(OH)2
  C-S-H + MgCl2  CaCl2 + M-S-H

## Slide 62: Chemical Mechanisms of Deicer Attack
How Calcium Chloride (CaCl2) Attacks
  3Ca(OH)2 + CaCl2 + 12H2O  3CaO·CaCl2·15H2O
How Sodium Chloride (NaCl) Attacks
  2NaCl + Ca(OH)2  CaCl2 + 2NaOH
How Magnesium Chloride (MgCl2) Attacks
  Ca(OH)2 + MgCl2  CaCl2 + Mg(OH)2
  C-S-H + MgCl2  CaCl2 + M-S-H

## Slide 63: Chemical Mechanisms of Deicer Attack
How Calcium Chloride (CaCl2) Attacks
  3Ca(OH)2 + CaCl2 + 12H2O  3CaO·CaCl2·15H2O
How Sodium Chloride (NaCl) Attacks)
  2NaCl + Ca(OH)2  CaCl2 + 2NaOH
How Magnesium Chloride (MgCl2) Attacks
  Ca(OH)2 + MgCl2  CaCl2 + Mg(OH)2
  C-S-H + MgCl2  CaCl2 + M-S-H

## Slide 64: Chemical Mechanisms of Deicer Attack
How Calcium Chloride (CaCl2) Attacks
  3Ca(OH)2 + CaCl2 + 12H2O  3CaO·CaCl2·15H2O
We did not find evidence of NaCl attack
How Magnesium Chloride (MgCl2) Attacks
  Ca(OH)2 + MgCl2  CaCl2 + Mg(OH)2
  C-S-H + MgCl2  CaCl2 + M-S-H
We found strong evidence of the magnesium chloride mechanism shown here

## Slide 65: Compressive strength evolution with time of mortar cubes
MgCl2 & MBAP ~60% loss
CaCl2 ~10% loss
NaCl & Control

## Slide 66: Length change of mortar bars
~0.8% expansion MBAP
~0.4% expansion MgCl2
~0.3% expansion CaCl2

## Slide 67: X-ray Diffractogram for Mortars Exposed to CaCl2 – 30 days @ 40 ºF
Calcium Oxychloride

## Slide 68: Typical Concrete Sorptivity with Different Fluids ( 0.55 w/c)
Chart: Time (s1/2)
| 0 | 7.7459666924148332 | 17.320508075688771 | 24.494897427831781 | 34.641016151377492 | 42.426406871192853 | 60 | 84.852813742385706 | 103.9230484541326 | 120 | 134.1640786499874 | 146.9693845669907 | 293.9387691339814 | 415.69219381653062 | 509.11688245431418 | 587.87753826796268 | 657.26706900619934 | 720 | 777.68888380894316 | 831.38438763306101 | 881.81630740194237 | 929.51600308977936
Water | 0 | 0.09658 | 0.18697 | 0.23773 | 0.3046 | 0.35536 | 0.4668 | 0.61415 | 0.73549 | 0.82712 | 0.91008 | 0.98437 | 1.6951 | 2.23 | 2.599 | 2.7971 | 2.9123 | 2.9667 | 2.9964 | 3.0175 | 3.0299 | 3.0534
CaCl2 | 0 | 0.086262 | 0.13802 | 0.1639 | 0.20164 | 0.23291 | 0.28143 | 0.36015 | 0.40975 | 0.44749 | 0.47983 | 0.5111 | 0.84537 | 1.0912 | 1.2799 | 1.4169 | 1.5258 | 1.6088 | 1.6789 | 1.7317 | 1.7824 | 1.8255
MgCl2 | 0 | 0.06861 | 0.10074 | 0.12035 | 0.13941 | 0.1552 | 0.1737 | 0.19874 | 0.21942 | 0.23411 | 0.25208 | 0.26786 | 0.43552 | 0.58903 | 0.70499 | 0.79319 | 0.86723 | 0.93474 | 0.99626 | 1.0469 | 1.0725 | 1.1433
NaCl | 0 | 0.073738 | 0.13166 | 0.16718 | 0.21528 | 0.25408 | 0.32949 | 0.42128 | 0.49887 | 0.5557 | 0.60051 | 0.64367 | 1.1097 | 1.4791 | 1.778 | 1.9993 | 2.1905 | 2.3041 | 2.3991 | 2.4783 | 2.54 | 2.5854
Water
NaCl
CaCl2
MgCl2

## Slide 69: Sorptivity of 15% MgCl2 into Different 0.45 w/c Concrete Mixtures
Chart: Time (s1/2)
| 0 | 7.7459666924148332 | 17.320508075688771 | 24.494897427831781 | 34.641016151377492 | 42.426406871192853 | 60 | 84.852813742385706 | 103.9230484541326 | 120 | 134.1640786499874 | 146.9693845669907 | 293.9387691339814 | 415.69219381653062 | 509.11688245431418 | 587.87753826796268 | 657.26706900619934 | 720 | 777.68888380894316 | 831.38438763306101 | 881.81630740194237 | 929.51600308977936
OPC | 0 | 0.033871 | 0.040425 | 0.04698 | 0.050259 | 0.056268 | 0.065008 | 0.081942 | 0.096147 | 0.10762 | 0.11909 | 0.12455 | 0.23491 | 0.32723 | 0.40262 | 0.45507 | 0.50642 | 0.55013 | 0.59383 | 0.63153 | 0.67086
fly ash | 0 | 0.036512 | 0.049041 | 0.052312 | 0.060484 | 0.062667 | 0.070295 | 0.082281 | 0.086096 | 0.095361 | 0.1019 | 0.10789 | 0.16348 | 0.20107 | 0.23812 | 0.26156 | 0.28608 | 0.30351 | 0.32422 | 0.33893 | 0.35855 | 0.37217
slag | 0 | 0.031221 | 0.046006 | 0.052031 | 0.055866 | 0.059693 | 0.066272 | 0.076668 | 0.083232 | 0.088705 | 0.095282 | 0.096372 | 0.1325 | 0.15933 | 0.17958 | 0.19272 | 0.20476 | 0.21571 | 0.22502 | 0.23542 | 0.24309 | 0.24911
35% slag
Type I PC
15% Fly Ash

## Slide 70: SCM Effects on Permeability
0.45 w/c OPC
0.45 w/c OPC + 15% Class F

## Slide 71: SCM Effects on Permeability
0.45 w/c OPC + 15% Class F
0.45 w/c OPC + 35% GBFS

## Slide 72: Take Aways – Chemical Attack
Brines of magnesium and calcium chloride have been demonstrated to react deleteriously with hydrated cement paste
  Expansive calcium oxychloride forms
  Reaction is slower than physical attack mechanisms

## Slide 73: Take Aways – Chemical Attack
Use of SCMs reduces susceptibility of concrete for chemical attack
  Reduces CH available to react
  Permeability of concrete not compromised by CH leaching
  Improves concrete strength (affects physical and chemical attack)

## Slide 74: Take Aways – Chemical Attack
The various brines penetrate concrete at different rates (sorptivity)
Sorptivity will impact chemical and physical attack
Although NaCl brines have demonstrated no chemical attack – they are the most sorptive, which impacts physical attack

## Slide 75: Curing Requirements
Adequate moisture
Adequate temperature
Adequate time

## Slide 76: Curing Affects Strength & Durability
Curing affects strength but for pavement or harsh exposures the affects on durability are more important
Curing critical when SCMs are used – slower to hydrate
PCA

## Slide 77: Curing Compounds
PCA
Reduce the rate of evaporation from the surface to a rate less than the rate water can move up through the concrete

## Slide 78: Moisture Retention
Curing compounds
  Reduce the rate of moisture loss
  Other physical materials (wet burlap, wet straw) will likely give better protection but are normally not practical for large, fast moving operations
  Depends on quality of film (membrane)
  Film thickness
  Requires complete coverage…

## Slide 79: Paint my house?

## Slide 80: Curing Effects
Protect the surface, which is most vulnerable to moisture loss (affects cement hydration at surface – strength)
Water moving up out of the concrete (loss) creates capillary pores increasing porosity and permeability
Increased hydration (water retained) results in lower permeability

## Slide 81: Curing Take Aways
Keep the water in so hydration occurs
The more complete hydration, the lower the permeability and higher strength
Not all curing compounds are equal in performance – unless you don’t use them

## Slide 82: Sealants

## Slide 83: Two General Classes
Film Formers
  Epoxies
  Polyurethanes
  Polyesters
  Waxes
  Acrylics
Chemically Reactive
  Silicates
  Silanes
  Siloxanes
Penetrate and react with CH to form calcium silicate

## Slide 84: Film Formers
Form complete surface barrier with little penetration
Do not react with concrete
Susceptible to wear and abrasion
In some cases susceptible to UV
Can be removed
Capable of penetrating and sealing large cracks
May be applied with aggregate top coat to improve friction
May be thinned (pore blocker)
Ex. epoxies, polyurethanes, methacrylates, waxes, acrylics

## Slide 85: Chemically Reactive – Water Repellent
React with cement paste (depending on chemistry) by bonding with Si
  methoxy vs ethoxy
In some cases susceptible to UV
Water enters pore but the water repellent coating prevents ingress into the cement paste
Allow moisture transport out of concrete
Ex. silanes, siloxanes

## Slide 86: Application Requirements
Affected by
  Climatic Conditions
  Surface Preparation
  Application Rates

## Slide 87: Application Requirements
Climatic Conditions
  Temperature (~40 – 90 ºF) at the concrete surface
  Wind can affect volatilization and curing rates
  Moisture: most not compatible with water
    Two days drying is a typical requirement
  Most sealers require curing time
    24 hrs typical

## Slide 88: Application Requirements
Surface Preparation
  Cure concrete adequately (28 days)
    Application at 3 – 6 months age often recommended
  Badly deteriorated concrete cannot be saved with a sealer
  Remove dirt/debris
    Avoid sandblasting the surface – increase permeability
  Silanes/siloxanes best applied to new concrete surface before carbonation has occurred – improves bond – sealant requires alkalinity to react

## Slide 89: Application Requirements
Application Rates
  Varies widely (100 - 300 ft2/gal)
    Film sealers may require more than recommended if aggregate is placed for friction
  Water repellent sealers must be applied to near saturation conditions at the surface
Other Considerations
  VOCs
    Most sealers are in an organic liquid form and the volatization of the organic media contributes VOCs

## Slide 90: Salt Ingress for OPC mixture

## Slide 91: Tri-siloxane 12% (aliphatic hydrocarbon)
PCC Mixtures

## Slide 92: Tri-siloxane 12% (aliphatic hydrocarbon)
Fly Ash Mixtures

## Slide 93: Tri-siloxane 12% (aliphatic hydrocarbon)
GBFS Mixtures

## Slide 94: Tri-silane 40% (2-propanol)
OPC Mixtures

## Slide 95: Tri-silane 40% (2-propanol)
Fly Ash Mixtures

## Slide 96: Tri-silane 40% (2-propanol)
GBFS Mixtures

## Slide 97: Summary
Keep fluids out of concrete and all materials-related distress is minimized
Materials selection is very important
  Low w/c
  Low paste content
  Use SCMs
Curing is essential
  Keep the mixture water in and allow the materials time to form dense, impermeable, hydration products

## Slide 98: Summary
Deicing chemicals are a serious concern
  Contribute to physical attack
  Contribute to chemical attack
Sealants may be required to offset deicing fluids
  Keep brines out
  Slow ingress of salt solutions

## Slide 99: Questions?
Contact:
Larry Sutter
Michigan Tech
Houghton MI
llsutter@mtu.edu